{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["封面","建筑负荷统计","系统热负荷统计","系统冷负荷统计","房间热负荷统计","房间冷负荷统计"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":30,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"封面","index":0,"n_rows":10,"n_cols":4,"rows_kept":10,"cut":false,"hidden":false,"merged":[[2,4,2,5],[1,1,1,4]]}
[]
[null,"DeST 模拟结果报表……负荷统计"]
[]
[]
[]
[]
[null,null,"模板编号：","DeST-M-007"]
[null,null,"建筑名称：","A"]
[null,null,"城市名称：","南京"]
[null,null,"报告日期：","2022-02-15"]

{"sheet":"建筑负荷统计","index":1,"n_rows":27,"n_cols":4,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
[]
[null,"季节设定","月份","日期"]
[null,"采暖季开始日期",11,15]
[null,"采暖季结束日期",3,15]
[null,"空调季开始日期",6,1]
[null,"空调季结束日期",8,31]
[]
[]
[null,"项目统计","单位","统计值"]
[null,"总建筑空调面积","m2",972.06658690193194]
[null,"项目负荷统计"]
[null,"  全年最大热负荷","kW",60.5801601059338]
[null,"  全年最大冷负荷","kW",33.882606020616393]
[null,"  全年最大加湿量","kg/h",7.6116567040038134]
[null,"  全年累计热负荷","kW·h",13348.516782850149]
[null,"  全年累计冷负荷","kW·h",2384.1677144910809]
[null,"  全年累计加湿量","kg",892.6161752724795]
[null,"项目负荷面积指标"]
[null,"  全年最大热负荷指标","W/m2",62.320998296020534]
[null,"  全年最大冷负荷指标","W/m2",34.856260339740167]
[null,"  全年最大加湿量指标","g/h/m2",7.8303861140448028]
[null,"  全年累计热负荷指标","kW·h/m2",13.73210123947695]
[null,"  全年累计冷负荷指标","kW·h/m2",2.4526794219824475]
[null,"  全年累计加湿量指标","kg/m2",0.91826649254279136]
[null,"项目分季节负荷指标"]
[null,"  采暖季热负荷指标","W/m2",11.003286258771798]
[null,"  空调季冷负荷指标","W/m2"]

{"sheet":"系统热负荷统计","index":2,"n_rows":4,"n_cols":7,"rows_kept":4,"cut":false,"hidden":false,"merged":[]}
[]
[null,"系统名称","系统面积","全年最大时刻","全年最大(W/m2)","采暖季累计（kW·H/m2）","采暖季平均(W/m2)"]
[null,"AC-19445",676.933290956326,583,83.339924582524972,17.933385107536008,20.613086330501158]
[null,"AC-19447",295.13329594560599,586,16.794346737775196,4.0958150016776642,3.2819030462160765]

{"sheet":"系统冷负荷统计","index":3,"n_rows":4,"n_cols":7,"rows_kept":4,"cut":false,"hidden":false,"merged":[]}
[]
[null,"系统名称","系统面积","全年最大时刻","全年最大(W/m2)","空调季累计（kW·H/m2）","空调季平均(W/m2)"]
[null,"AC-19445",676.933290956326,688,44.317170264515887]
[null,"AC-19447",295.13329594560599,690,20.756895780543775]

{"sheet":"房间热负荷统计","index":4,"n_rows":20,"n_cols":14,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
[]
[null,"房间名称","房间功能","房间面积","全年最大时刻","全年最大(W/m2)","房间全年最大(kW)","加湿量(kg/h)","室内显热负荷(kW)","新风显热负荷(kW)","室内发热量(kW)","采暖季累计(kW·h/m2)","采暖季平均(W/m2)","层数"]
[null,"R1-5657","大堂门厅",186.34176693010829,582,56.63278486547194,10.553053198004736,0,9.0839052200317383,1.4691481590270996,4.1926898956298828,13.77343893785603,5.9573697828097014,1]
[null,"R1-5660","展览厅",62.643644001550378,559,90.164583665552868,5.6482380806928978,0,4.1686625480651855,1.4795757532119751,0,10.381243013235,5.3456452179376939,1]
[null,"R1-5663","展览厅",30.842116624989554,560,75.112482784502646,2.3166279540321506,2.7825422585010529E-2,1.5053908824920654,0.81123703718185425,1.5000766515731812,7.2133500446685597,3.7143924019920491,1]
[null,"R1-5666","展览厅",30.510382331169147,560,75.645755510121774,2.3079809223439605,2.7526203542947769E-2,1.5054694414138794,0.80251145362854004,1.4839420318603516,7.9808246284569835,4.1095904368985492,1]
[null,"R1-5669","酒店客房（三星以下）",32.675156565260316,586,22.071826782224683,0.72120039579049733,5.5239807814359665E-2,0.37895461916923523,0.34224578738212585,0.21111574769020081,7.3596080939098263,2.534300307820188,1]
[null,"R1-5675","酒店客房（三星以下）",32.784402499819358,586,21.884835927037397,0.71748126967450132,5.5424496531486511E-2,0.37409123778343201,0.34339004755020142,0.21182160079479218,7.2044057214293202,2.4808559646795181,1]
[null,"R1-5678","酒店客房（三星以下）",32.873736879607115,586,14.676737173363547,0.48247919608830192,5.5575523525476456E-2,0.13815344870090485,0.34432575106620789,0.21239879727363586,2.5707304708365668,0.88523776543958899,1]
[null,"R2-5703","办公室",63.846434835598302,583,180.70828556866053,11.537579778812173,0.37799906730651855,9.9696187973022461,1.5679609775543213,0,52.502965014471179,24.261998620365613,1]
[null,"R2-5706","办公室",30.560978048503124,559,134.71914563327115,4.1171488524114945,0.13124571740627289,3.4835078716278076,0.63364094495773315,0,42.965953780775571,19.854876978177249,1]
[null,"R2-5709","办公室",30.975809701909593,559,134.05254265356675,4.1523860512940027,0.13302722573280334,3.5101439952850342,0.6422419548034668,0,40.218168961358835,18.585105804694468,1]
[null,"R2-5712","多功能厅",164.6741584128952,175,72.311875186079448,11.907897189525952,2.2341327667236328,7.6980342864990234,4.2098627090454102,2.3728742599487305,20.810760925369731,8.8330903757936028,1]
[null,"R2-5718","酒店客房（三星以下）",32.799999999884271,560,11.177853067854805,0.36663358062434398,0,6.4676322042942047E-2,0.30195724964141846,0.2602706253528595,1.0647768620439189,0.36665869905093629,1]
[null,"R2-5724","酒店客房（三星以下）",32.800000000640189,560,11.769811095857635,0.38604980395166533,0,8.409254252910614E-2,0.30195724964141846,0.2602706253528595,1.221998672590523,0.42079844097469798,1]
[null,"R2-5727","酒店客房（三星以下）",32.800000000297331,562,3.770378935944362,0.12366842910009612,1.7013266682624817E-2,-0.16288284957408905,0.28655126690864563,0.21192237734794617,2.3581602087984661E-2,8.120386393934113E-3,1]
[null,"R3-5733","酒店客房（三星以下）",32.799999999884271,586,26.273433830501922,0.86176862963742251,5.5450864136219025E-2,0.51821523904800415,0.34355342388153076,0.21192237734794617,8.788570517636952,3.0263672581394463,1]
[null,"R3-5736","酒店客房（三星以下）",32.800000000328922,586,25.514552108995797,0.83687730918345449,5.5450864136219025E-2,0.49332389235496521,0.34355342388153076,0.21192237734794617,8.6004705897737548,2.9615945557072161,1]
[null,"R3-5739","酒店客房（三星以下）",32.799999999884214,586,18.19562988968174,0.59681666037945436,5.5450864136219025E-2,0.25326323509216309,0.34355342388153076,0.21192237734794617,3.6922298281061439,1.2714290041687824,1]
[null,"R3-5742","多功能厅",76.538000069602461,175,107.05452055255041,8.1937389015023623,1.0383903980255127,6.2370595932006836,1.956679105758667,1.1028752326965332,34.863848182071777,14.797898209707887,1]

{"sheet":"房间冷负荷统计","index":5,"n_rows":20,"n_cols":14,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
[]
[null,"房间名称","房间功能","房间面积","全年最大时刻","全年最大(W/m2)","房间全年最大(kW)","除湿负荷(kW)","室内显热负荷(kW)","新风显热负荷(kW)","室内发热量(kW)","空调季累计(kW·h/m2)","空调季平均(W/m2)","层数"]
[null,"R1-5657","大堂门厅",186.34176693010829,1195,15.328335381395712,2.8563090990665723,-2.856309175491333,-0.48574471473693848,0.6439245343208313,5.1457161903381348,0,0,1]
[null,"R1-5660","展览厅",62.643644001550378,688,115.71782317373659,7.2489861195299117,0,-8.0308074951171875,0.78182125091552734,3.1990857124328613,0,0,1]
[null,"R1-5663","展览厅",30.842116624989554,688,112.6270442959601,3.4736564353038664,0,-3.8585801124572754,0.38492369651794434,1.5750452280044556,0,0,1]
[null,"R1-5666","展览厅",30.510382331169147,688,112.48180523540988,3.4318628830324589,0,-3.8126463890075684,0.38078349828720093,1.5581041574478149,0,0,1]
[null,"R1-5669","酒店客房（三星以下）",32.675156565260316,692,12.844751820898214,0.41970427678976163,0,-0.60233765840530396,0.18263339996337891,1.4533431529998779,0,0,1]
[null,"R1-5675","酒店客房（三星以下）",32.784402499819358,692,13.311292224258182,0.43640276207279588,0,-0.61964678764343262,0.1832440197467804,1.4582022428512573,0,0,1]
[null,"R1-5678","酒店客房（三星以下）",32.873736879607115,690,20.555331084571108,0.67573054554739975,0,-0.84557729959487915,0.1698467880487442,1.4188144207000732,0,0,1]
[null,"R2-5703","办公室",63.846434835598302,688,124.35325494151562,7.9395119882180198,0,-8.6656579971313477,0.72614586353302002,2.793971061706543,0,0,1]
[null,"R2-5706","办公室",30.560978048503124,688,89.114025050870396,2.7234117633934076,0,-3.0709915161132813,0.34757974743843079,1.337372899055481,0,0,1]
[null,"R2-5709","办公室",30.975809701909593,688,89.363920069895599,2.7681197823017456,0,-3.120417594909668,0.35229778289794922,1.3555262088775635,0,0,1]
[null,"R2-5712","多功能厅",164.6741584128952,1241,13.395109536441014,2.2058283897619706,0,-4.0455718040466309,1.8397432565689087,5.8977060317993164,0,0,1]
[null,"R2-5718","酒店客房（三星以下）",32.799999999884271,690,27.584850920099573,0.9047831101760736,0,-1.0742489099502563,0.1694658100605011,1.4156320095062256,0,0,1]
[null,"R2-5724","酒店客房（三星以下）",32.800000000640189,690,28.028570237666152,0.9193371038133934,0,-1.0888029336929321,0.1694658100605011,1.4156320095062256,0,0,1]
[null,"R2-5727","酒店客房（三星以下）",32.800000000297331,690,34.058476504976156,1.1171180293733447,0,-1.2865837812423706,0.1694658100605011,1.4156320095062256,0,0,1]
[null,"R3-5733","酒店客房（三星以下）",32.799999999884271,1244,17.913541670691178,0.58756416679659751,0,-0.78476077318191528,0.19719657301902771,1.4588959217071533,0,0,1]
[null,"R3-5736","酒店客房（三星以下）",32.800000000328922,1244,16.855209629606133,0.55285087585662518,0,-0.75004744529724121,0.19719657301902771,1.4588959217071533,0,0,1]
[null,"R3-5739","酒店客房（三星以下）",32.799999999884214,1242,23.592137834474684,0.77382212096803804,0,-0.94174730777740479,0.16792520880699158,1.4156320095062256,0,0,1]
[null,"R3-5742","多功能厅",76.538000069602461,1241,33.302164995317519,2.5488811067295249,0,-3.4039652347564697,0.85508418083190918,2.7411625385284424,0,0,1]